## Sheet1
STATE BANK OF INDIA KOLKATA CIRCLE
NAME OF THE BRANCH |  |  |  | Naktala Branch
S.No. | Description of the work | Unit | Qty | Rate (Rs) | Amount (Rs)
ELECTRICAL WORK SCHEDULE FOR ALTERNATIVE PREMISES NAKTALA BRANCH
1 | Supply and installation(Concelaed) of Double door 4way VTPN DB (LEGRAND/SIEMENS/HAGER/ABB)with MCB having breaking capacity of 25 KA. a) incoming- 1 No ...125amp ,25KA,4P MCCB b)outgoing - 1 Nos. 63 Amp TP MCB and 9 Nos. 20-32 Amp SP MCB C series (glow sign and Acs) Necessary blanking plate as required.(As per IS8828-96Latest) (MAIN DB) | Nos. | 1 | 18500 | 18500
2 | Supply and installation(Concelaed) of Double door 6way TPN DB (LEGRAND/SIEMENCE/HAGER/ABB/ Schnider) with MCB having breaking capacity of 10KA. a) incoming- 1 No ... 63 A ,16KA,4P MCB b)outgoing - 2nos. 40ATP MCB, 12 Nos. 20-32 Amp SP MCB C series necessary blanking plate as required.(As per IS8828-96Latest) | Nos. | 1 | 12500 | 12500
3 | Supply & installation of TPN front operated switch disconnector fuse units complete along with HRC fuses, statutory caution board, earthing etc. by MS legs on wall (L &T/ABB/SIEMENS 3KL)including interconnection with suitable size of copper wire with TPN DB/terminal block/Gland Box
| a) 63A | Nos. | 1 | 5500 | 5500
| b) 125A | Nos. | 1 | 7500 | 7500
4 | Supply & fixing of 63 Amp FP ON Load Change over (Front handle)(HPL/Havells EURO/Siemens/L&T/ABB) including interconnection with suitable size of copper. | Nos. | 1 | 6500 | 6500
5 | Supply & installation of 1.1 KV Grade PVC insulated and sheathed armoured AL cable with GI earth continuity wire by MS bar saddles on wall ( GLOSTER/Havells/NATIONAL) ( CESC TO main panel)
| a) 4C x 35 sq.mm.(VTPN Panel) | Mtrs | 50 | 325 | 16250
| b) 4C x 25 sq.mm.(DG, TPN DB,COS etc.) | Mtrs | 100 | 220 | 22000
6 | End connection of above cable with heavy duty nickle plated brass compression gland crimping type socket insulation tape etc. with all concern.
| a)4C x 35 sq.mm. | Nos. | 4 | 220 | 880
| b)4C x 25 sq.mm. | Nos. | 16 | 185 | 2960
7 | Supply & installation(concealed) of double door 12way SPN MCB DB with following accessories a)1 No. 32 amp. 100 mA DP RCBO as incomer b)10 Nos. 6-20 Amps SP MCB Make: Legrand / Siemens/Hager/Crabtree/ABB, (LDB, UPS DB) | Nos. | 6 | 6500 | 39000
UPS ROOM
8 | Supply & fixing on wall industrial Plug & socket DB with hyalm(or ISI approved) cover one 32 Amps industrial socket (3P+N+E) but with 32Amps DP MCB (Legrand)duly inter connected. (UPS incoming) | Nos. | 2 | 5500 | 11000
| Supply & fixing on wall industrial Plug & socket DB with hyalm(or ISI approved) cover one 32 Amps industrial socket (P+N+E) but with 32Amps DP MCB (Legrand)duly inter connected. (UPS outgoing) | Nos. | 2 | 4000 | 8000
9 | Supply & installation of 16 SWG thickness sheet steel enclosure including the following duly interconnected with 2nos. 32 A DP OFF load change over switch and distribution in various areas. i) 5 Nos. 25 mm x 6 mm tinned copper bus bars (Ph-2,N-2,E-1) ii) 4 Nos. 32 Amp SPN MCB and 2 Nos. neutral connector and 2 Nos. neutral (Legrand/Siemence/Schnider) UPS Changeover | Nos. | 1 | 13500 | 13500
| Supply & installation (AC-Timer DB) of 4 hours automatic power switching controller for AC with electronic timer and manual in double door power coated MS box (Make Legrand/Siemens/Hager/Crabtree Xpro) . The power controller will be required to regulate cyclic operation of 2 ACs at the interval of 4 hours and should include the following: i) One no.32 Amps. double pole 100 mA sensitivity RCBO MDS ( Legrand/Hager/Crabtree Xpro/Siemens make.) ii) One no. electronic MicroRex time switch QT31 (Legrand/Hager/Crabtree Xpro/Siemens make ) with 24 hour programming. iii) Two Nos.3 pole A.C contactor with 2 NO contacts Siemens 3TF33 or L&T iv)Two Nos.20 Amps. DP MCB C series for 2 Nos. ACs v) Necessary interconnections. vi) 2 Nos 6Amps modular type Switch vii) two nos LED indicator for AC. ( for UPS/System Room AC's) | Nos. | 1 | 14000 | 14000
7 | Distribution wiring(concealed/partly surface) including new point wiring 660 volt grade 3x1.5 sq.mm. (cu) PVC flexible wire in 20 SWG Rigid PVC (ISI Marked) conduit along with Conduit accessories circular boxes, MS boxes, 6 Amps Modular Type switch with socket outlets 6 pin, all individual control switch etc. Conduit size & nos of wires in conduit as per code of practice with circuit wiring with (2x2.5 + 1X1.5) sq.mm. copper wire from MCB DB to respective sw board. N.B. (I)Earth & neutral may be looped but from the last point earth & Neutral has to be connected with sw board. (ii)Point wiring should be inclusive of continuous wire length up to the connection block of light fittings/fans. PVC CONDUIT: BEC /NIC/AKG WIRE : FINOLEX/MESCAB/HAVELLS/RRKABLE Switch- LEGRAND Miling/CRABTREE/NW
| a) Light point(one switch controls one light) | Nos | 42 | 675 | 28350
| b)Light point(one switch control two lights) | Nos. | 23 | 825 | 18975
| c)Ceiling Fan point with regulator | Nos | 1 | 975 | 975
| d)Exaust fan | Nos | 8 | 800 | 6400
| e)Bracket Fan point with 6 amp 5pin socket | Nos. | 18 | 850 | 15300
| f)Call bell (with supply and fixing call bell) | Nos | 2 | 800 | 1600
| g)Board plug point 5 pin 5 Amps with switch. | Nos. | 15 | 300 | 4500
8 | Point wiring with 660 V grade PVC insulated multi stranded copper wire through ISI marked minimum 2 mm thick PVC conduit with junction box ,circular box, elbows ,bends, couplers and other accessories concealed ( below the false ceiling) or by chase cutting on wall /floor or on surface by bar saddles : PVC CONDUIT: BEC /NIC/AKG WIRE : FINOLEX/NATIONAL/HAVELLS/RRKABLE/ /MESCAB
| a)2X2.5 sq mm +1X1.5 sq mm in 20 mm dia conduit (For UPS and power sockets) | Mtrs. | 280 | 140 | 39200
| b)2X4 sq mm +1X2.5 sq mm in 20 mm dia conduit (AC points) | Mtrs. | 180 | 185 | 33300
| c)2X6 sq mm +1X2.5 sq mm in 20 mm dia conduit (UPS i/p, o/p,& DB /LDB Incoming) | Mtrs. | 150 | 250 | 37500
9 | Supply & installation of MS Flush Metal box with front plate enclosing the following duly interconnected : Make:(Crabtree/PHILIPS/Legrand/NW ) a) 2 Nos 16 amp switch & 2 Nos 6 amps and 1 no. 6/16 amps socket outlet with indicator b) 1 No. mounting box c) 1 No. front plate ( 2 Nos at SWO/Service/Manager Room for UPS power) | Sets | 24 | 1000 | 24000
10 | Distribution wiring including new point wiring 660 volt grade 2x2.5+1x1.5 sq.mm. (copper ) PVC insulated flexible wire in 20 SWG Rigid PVC (ISI Marked) conduit along with Conduit accessories circular boxes, MS boxes, 2x 6 Amps + 2x6Amps modular type switch and socket(RAW POWER at SWO,BM.)(Crabtree/PHILIPS/Legrand/NW ) | Sets | 10 | 1750 | 17500
11 | Distribution wiring including new point wiring 660 volt grade 2x1.5+1x1.5 sq.mm. (copper ) PVC insulated flexible wire in 20 SWG Rigid PVC (ISI Marked) conduit along with Conduit accessories circular boxes, MS boxes, 1x 6 Amps + 1x6Amps modular type switch and socket (NON UPSPOWER).(Crabtree/PHILIPS/Legrand/NW ) | Sets | 8 | 1150 | 9200
12 | Supply & installation of MS Flush metal box with front plate enclosing the following duly interconnected make:( Crabtree /Legrand/ Philips) a) 1 Nos 16 amp switch & 1 Nos 6/16 amps socket outlet with indicator b) 1 No. mounting box c) 1 No. front plate for kitchen, safe/ locker, Record room, printer, swayam etc. | sets | 10 | 550 | 5500
13 | S& F 32 amps DP MCB C series(legrand//siemens /Hager) in Box with cover including interconnection with suitable size of copper wire) this sw will control Raw power DB incoming (to be installed near back gate Exit) for both floor | set | 2 | 1650 | 3300
FANS
14 | Supply & Installation of 12" dia Exaust fan 900 rpm with louver including hole cutting EPC/Crompton/Bajaj/havells) | Nos | 8 | 1750 | 14000
15 | Supply & Installation of 48" high speed, double ball bearing Ceiling fan EPC/Crompton/Bajaj/havells) | Nos | 7 | 2150 | 15050
16 | Supply & Installation of 16'' high speed, double ball bearing wall mounted fan EPC/Crompton/Bajaj/havells) | Nos. | 18 | 2250 | 40500
LIGHT FITTINGS
17 | S&F Philips make 39W RC380HE 6500K LED light fitting, 600x600 suitable for recess mounting,CRCA sheet, asthetic looking or eqv Crompton Greaves/Wipro/jaguar/havells | Nos. | 24 | 3950 | 94800
18 | S & F Philips make DNI92B LED9S-6500PSU WH downlighter or eqv. Crompton greaves/ wipro/jaguar/havells | Nos. | 46 | 1650 | 75900
19 | Supply & installation of the following following LED luminaries and lamps fittings with downrods circular boxes, ball sockets,ceiling plates etc. including connection with wire
| a)S & F Philips make 36W BN 208C Gen II including lamp. (Safe Room/Locker room etc.) or equv./Wipro/CG/Havells/jaguar | Nos | 24 | 1050 | 25200
22 | Supplying and fixing of angular /batten holder with 9 W LED lamp(Orpat/Philips/Havells) on wall or ceiling with necessary interconnection. | Nos. | 6 | 450 | 2700
BEMS CONDUIT WIRING (LOCKER / RECORD ROOM/ STATIONARY)
23 | Point wiring for Branch with 660Vgrade PVC insulated copper wire ( FRLS) 3 x 1.5 sq.mm. in 16 SWG MS conduit (ISI Marked) conduit alongwith conduit accessories circular boxes, MS boxes, 6 Amps Modular type Switch socket outlets 6 pin, all individual control switch etc. Conduit size & nos of wires in conduit as per code of practice with circuit wiring with (2x2.5 +1X1.5) sq.mm. copper wire from MCB DB.)
| a)Fluorescent Point | Nos. | 13 | 850 | 11050
| b)Fan Point with regulator | Nos. | 5 | 1000 | 5000
| c) Board plug point 5 pin 5 Amps socket & switch. | Nos | 5 | 325 | 1625
EARTHING
24 | Earthing as per IE 3043 Rules including making of 1 No. earth station with 50 mm dia 3 mts. length GI pipe (Class B) buried at an average depth of 3 mts. below ground level with 7/14 stranded earth lead wire upto earth busbar including providing masonary inspection pit and restoration of surface duly rammed. | Nos. | 5 | 5500 | 27500
25 | S&F Tinned copper Earth Bar on insulator (25 mm x6mmx3mm) | Nos. | 2 | 600 | 1200
26 | S&F 2x 2.5 PVC Armored copper Cable for Generator Neutral, CBS, VSAT earthing (From Earth station to 16 Amp VSAT sw at system room) National/INCAB/CCI/Gloster /Havells)(CONCEALED WHERE NECESSARY) | Mtrs | 60 | 250 | 15000
OTHER MISCELENEOUS
27 | Supply & fixing RJ-11 telephone socket (legrand/havells/NW) | Nos. | 5 | 350 | 1750
28 | Supplying and laying and connection of PVC insulated copper conductor of size 2 pair x 0.5 sq.mm.in 20 mm dia heavey duty PVC conduit(ISI marked) | Mtrs | 120 | 80 | 9600
29 | Supply and fixing of modular type 20A MCB operated sockets with 20A SPMCB for AC points | Nos | 9 | 1650 | 14850
30 | S&F 32 amps DP MCB in MS Box with one no. microrex time switch QT31 and one 2 pole 20 amp contactor. ( for Glow sign) (Legrand / Hager/havells) | Nos. | 1 | 4500 | 4500
31 | Supply & fixing 16 amp plug top with indicator socket (legrand/havells/NW/Crabtree) | Nos. | 5 | 850 | 4250
32 | Supply & fixing 3cx2.5 sq.mm. PVC insulated multistrand flexible cable (Gloster/Mescab/National/ finolex/Rajnigandha) | Mtrs. | 15 | 200 | 3000
33 | Marking & painting of electrical DBs,SFU,and individual circuit in UPS DB,LDB of switch board and UPS power etc. and removing of old wires, cables, conduits and fixtures etc. & supply temporary power to sockets in table if necessary | LS | 1 | 2500 | 2500
793665
| Total amount (excluding GST) |  |  |  | 793665
Name Of the Contractor :
Address Of the Contractor :
Contractors license No Valid up to:
Phone No/Mobile No.
Supervisory certificate No. Valid up to:
Service tax Reg. No.
VAT No : |  | PAN NO:

## Sheet2
Nagrakata Branch AC Estimation
Sl. No. | Description of Item | Unit | Qnty | Rate | Amount
1 | PART A-EQUIPMENT
Supply, testing and Commissioning of Hi-wall split air conditioners air cooled type with evaporator coil,fan and fan motor air cooled condenser with scroll/Rotary compressor, condenser coil etc .The units shall be of following capacities . Make: Hitachi/Bluestar/Voltas/Daikin/Carrier
1.1 | 1.0 TON FIVE STAR split AC with 3.0 KVA voltage stabilizer ( Server room) | Nos. | 2 | 33500 | 67000
1.2 | 1.5 TON FIVE STAR split AC with 5.0 Kva voltage stabilizer (in Banking hall, manager cabin) | Nos. | 7 | 42500 | 297500
| Sub Total-A |  |  | RS. | 364500
2 | PART B-ANCILLIARY WORK
2.1 | Providing,fixing and testing of additional copper refrigerant piping of approved sizes for split units duly insulated with 9mm thick aluminium laminated nitrile rubber / Polyethylene insulation pipe section with interconnecting cabling for (BEYOND 3M. IF EXTRA REQUIRE):
A | For Hi-Wall Units | Rmt. | 30 | 475 | 14250
2.2 | Providing and fixing in position the PVC pipe for condesate drain cut to required lengths and installed with all screwed joints duly insulated with 6mm thick nitrile rubber / Polyethylene insulation pipe section .
A | 25mm dia | Rmt. | 30 | 105 | 3150
2.3 | Supply and fixing of M.S. angle iron frame work for outdoor units including painting of the same for:
A | Hi-Wall 1.0 TON | Nos. | 2 | 2000 | 4000
B | Hi-Wall 1.5 TON | Nos. | 7 | 2000 | 14000
| Sub Total-B |  |  | RS. | 35400
3 | PART C-ELECTRIC CABLES (IDU to ODU)
A | Providing & Fixing 3c x 2.5 sq.mm unarmoured copper wire cord (2.0 Ton) | Rmt. | 40 | 120 | 4800
| Sub Total-C |  |  | RS. | 4800
| GRAND TOTAL | 404700

## Sheet3
NEW Ballygunge(Kasba) Load Details
Electrical Gadgets | Qty | Connected Load in kW | Actual Load (0.8*Connected load)
Split Ac 1.0T | 2 | 2.5 | 2
Split AC 1.5T | 7 | 13.125 | 10.5
LED Light | 24&46 | 1.65 | 1.32
Tube lights & CFL | 24 | 0.864 | 0.6912
Fans | 33 | 2.145 | 1.716
UPS | 2 | 10 | 8
Rawpower | 28 | 5.6 | 4.48
|  | 35.884 | 28.7072
Power Supply Required: | 36KW
DG Set Capacity | 25KVA | 19.9572